## all
Model		Vitocal200S WO1C Rev.C			V333MW1			V100GC1			VDensHO1			V200GW1			V200KW2 / KW1			V200KO1B, KO2B			VScotHO1			VPlusHO1			V200WO1, VBC700			VBC550
		addr	fact.	bytes	addr	fact.	bytes	addr	fact.	bytes	addr	fact.	bytes	addr	fact.	bytes	addr	fact.	bytes	addr	fact.	bytes	addr	fact.	bytes	addr	fact.	bytes	addr	fact.	bytes	addr	fact.	bytes
equipment identity		0x00F8	204D		0x00F8	20B8	2	0x00F8	20A0	2	0x00F8	20C2	2	0x00F8	20A4	2	0x00F8	2098	2	0x00F8	209f	2	0x00F8	20CB	2	0x00F8	20C8	2	0x00F8	2046-2047-2049		0x00F8	2032-2033

Temperatures (actual values)
Outside temperature (sensor 1)	ATS	0x0101	/ 10	2	0x0800	/ 10	2							0x0800	/ 10	2	0x0800	/ 10	2	0x0800	/ 10	2							0x0101	/ 10	2	0x0800	/ 10	2
Boiler temperature (sensor 3)	KTS				0x0802	/ 10	2	0x0802	/ 10	2				0x0802	/ 10	2	0x0802	/ 10	2	0x0802	/ 10	2
Storage temperature (sensor 5)	STS1				0x0804	/ 10	2	0x0804	/ 10	2				0x0804	/ 10	2	0x0804	/ 10	2	0x0804	/ 10	2							0x010B	/ 10	2	0x0804	/ 10	2
Storage temperature 2 (sensor 5B)	STS2				0x0806	/ 10	2	0x0806	/ 10	2				0x0806	/ 10	2							0x0806	/ 10	2							0x0806	/ 10	2
Hot water temperature above		0x010D	/ 10	2																									0x010D	/ 10	2
Domestic water temperature below																													0x010E	/ 10	2
Exhaust gas temperature (sensor 15)	AGTS							0x0808	/ 10	2				0x0808	/ 10	2	0x0808	/ 10	2				0x0808	/ 10	2							0x0808	/ 10	2
Return temperature (17A)	RLTS	0x0106	/ 10	2	0x080A	/ 10	2	0x080A	/ 10	2	0x0808	/ 10	2	0x080A	/ 10	2	0x080A	/ 10	2
Flow temperature (17B)	VLTS	0x0105	/ 10	2	0x080C	/ 10	2	0x080C	/ 10	2				0x080C	/ 10	2	0x080C	/ 10	2
Flow temperature system					0x0950	/ 10	2																						0x010A	/ 10	2
Outside temperature low					0x5525	/ 10	2				0x5525	/ 10	2	0x5525	/ 10	2	0x5525	/ 10	2				0x5525	/ 10	2	0x5525	/ 10	2				0x080E	/ 10	2
Outside temperature dampened					0x5527	/ 10	2				0x5527	/ 10	2	0x5527	/ 10	2	0x5527	/ 10	2				0x5527	/ 10	2	0x5527	/ 10	2
Boiler temperature boiler1					0xA202	/ 100	2
Boiler temperature boiler2					0xA242	/ 100	2
Boiler temperature boiler3					0xA282	/ 100	2
Boiler temperature boiler4					0xA2C2	/ 100	2
Flow temperature A1M1					0x2900	/ 10	2																									0x2900	/ 10	2
Flow temperature M2					0x3900	/ 10	2				0x3900	/ 10	2				0x3900	/ 10	2				0x3900	/ 10	2	0x3900	/ 10	2	0x0114	/ 10	2
Flow temperature M3					0x4900	/ 10	2																						0x0115	/ 10	2
Return temperature M2																	0x3902	/ 10	2
boiler temperature								0xA309	/ 100	2	0xA393	/ 100	2	0xA309	/ 100	2	0xA309	/ 100	2

Boiler temperature low					0x0810	/ 10	2	0x0810	/ 10	2	0x0810	/ 10	2	0x0810	/ 10	2	0x0810	/ 10	2				0x0810	/ 10	2	0x0810	/ 10	2
Storage temperature low	STS1				0x0812	/ 10	2	0x0812	/ 10	2	0x0812	/ 10	2	0x0812	/ 10	2	0x0812	/ 10	2	0x0812	/ 10	2	0x0812	/ 10	2	0x0812	/ 10	2				0x0814	/ 10	2
Storage temperature 2 low	STS2				0x0814	/ 10	2	0x0814	/ 10	2	0x0814	/ 10	2	0x0814	/ 10	2	0x0814	/ 10	2				0x0814	/ 10	2	0x0814	/ 10	2
Exhaust gas temperature low	AGTS							0x0816	/ 10	2				0x0816	/ 10	2	0x0816	/ 10	2							0x0816	/ 10	2
Return temperature (17A) lowpass					installed 0x0818	/ 10	2	installed 0x0818	/ 10	2				installed 0x0818	/ 10	2	installed 0x0818	/ 10	2							installed 0x0818	/ 10	2
Return / flow temperature (17B) Low pass					0x081A	/ 10	2	0x081A	/ 10	2				0x081A	/ 10	2	0x081A	/ 10	2
Room temperature A1M1 lowpass	RTS				0x0896	/ 10	2							0x0896	/ 10	2	0x0896	/ 10	2				0x0896	/ 10	2
Room temperature M2 low-pass	RTS_M2				0x0898	/ 10	2																0x0898	/ 10	2
Room temperature M3 lowpass					0x089A	/ 10	2
Maximum exhaust gas temperature reached								0x089F	/ 10	2				0x089F	/ 10	2	0x089F	/ 10	2

Temperatures (actual setpoints)
Pre-setpoint temperature system		0x1800		2	0x5600	/ 10	2
Pre-flow setpoint temperature A1M1					0x2544	/ 10	2	0x2544	/ 10	2	0x2544	/ 10	2	0x2544	/ 10	2	0x2544	/ 10	2				0x2544	/ 10	2
Room temperature temperature actual M2																							0x350C	/ 10	2
Pre-flow setpoint temperature M2					0x3544	/ 10	2				0x3544	/ 10	2										0x3544	/ 10	2
Pre-flow setpoint temperature M3					0x4544	/ 10	2																						0x1004	/ 10	2
Return flow temperature system					0x56A0	/ 10	2
Boiler temperature								0x555A	/ 10	2	0x555A	/ 10	2	0x555A	/ 10	2	0x555A	/ 10	2	0x5502 0x6300	/ 10 /10	2 2	0x555A	/ 10	2	0x555A	/ 10	2
Boiler boiler temperature boiler1					0xA226	/ 100	2
Boiler boiler temperature boiler2					0xA266	/ 100	2
Boiler boiler temperature boiler3					0xA2A6	/ 100	2
Boiler boiler temperature boiler4					0xA2E6	/ 100	2

burner
Current level (burner status)								0x551E	0..2	1				0x551E	0..2	1	0x551E	0..2	1
Current performance (0..100%)								0x55E3	/ 2	1				0x55E3	/ 2	1	0x55E3	/ 2	1				0xA38F	/ 2	1
burner fault								0x0883	0..1	1				0x0883	0..1	1	0x0883	0..1	1
Condition 1st stage								0x0842	0..1	1				0x0842	0..1	1	0x0842	0..1	1
Condition 2nd stage								0x0849	0..1	1				0x0849	0..1	1	0x0849	0..1	1
oil consumption								0x7574	/ 1000	4				0x7574	/ 1000	4	0x7574	/ 1000	4	0x7574	/ 1000	4
burner starts								0x088A		4	0x088A		4	0x088A		4	0x088A		4	0x088A		4	0x088A		4	0x088A		4				0x088A		4
Operating hours Stage 1								0x0886	sec	4	0x0886	sec	4	0x0886	sec	4	0x08A7	sec	4	0x8A7	sec	4	0x08A7	sec	4	0x0886	sec	4				0x08A7	sec	4
Operating hours Stage 2								0x08A3	sec	4				0x08A3	sec	4	0x08AB	sec	4

Solar
collector temperature											0x6564	/ 10	2							0x6564	/ 10	2	0x6564	/ 10	2				0x0111	/ 10	2	0x6564	/ 10	2
operating hours											0x6568		2							0x6568		2	0x6568		2							0x6568		2
reheating											0x6551	0..1	1							0x6551	0..1	1	0x6551	0..1	1
solar pump											0x6552	0..1	1										0x6552	0..1	1
storage temperature											0x6566	/ 10	2							0x6566	/ 10	2	0x6566	/ 10	2				0x0113	/ 10	2
Storage temperature																																0x081A	/ 10	2
heat											0x6560	kWh	4							0x6560	kWh	4	0x6560	kWh	4							0x6560	kWh	4
Solar Info																							0x7754		1

Solar day contract																				0xCF30	Wh	4
States Pumps, mixers, etc.
Cylinder primary pump					0x0845	0..1	1				0x6513	0..1	1	0x0845	0..1	1	0x0845	0..1	1	0x0845	0..1	1	0x0845	0..1	1
circulation pump					0x0846	0..1	1				0x6515	0..1	1	0x0846	0..1	1	0x0846	0..1	1				0x0846	0..1	1
Mixing position M1 (0..100%)					0x254C	/ 2	1							0x254C	/ 2	1	0x254C	/ 2	1				0x254C	/ 2	1
Mixing position M2 (0..100%)					0x354C	/ 2	1
Mixing position M3 (0..100%)					0x454C	/ 2	1
Heating circuit pump A1M1					0x2906	0..1	1				0x7663	0..1 0..100	2	0x2906	0..1	1	0x2906	0..1	1
Heating circuit pump M2					0x3906	0..1	1				0x7665	0..1 0..100	2										0x3906	0..1	1
Heating circuit pump M3					0x4906	0..1	1
Throttle valve position (0..100%)								0x5555	/ 2	1				0x5555	/ 2	1	0x5555	/ 2	1				0x5555	/ 2	1
Internal pump											0x7660	0..1 0..100	2
switching valve											0x0A10	0..3	1
Nominal speed of heating circuit pump M2											0x0A3B	0..100	1										0x0A3B	0..100	1
Set speed Internal pump											0x0A3C	0..100	1										0x0A3C	0..100	1

Operating conditions (read only)
collective fault					0x0847	0..1	1	0x0847	0..1	1	0x0A82	0..1	1	0x0847	0..1	1	0x0847	0..1	1				0x0847	0..1	1
Current operating mode A1M1					0x2500		22	0x2500		22	0x2500		22	0x2500		22	0x2500		22				0x2500		22	0x2500		22
Current operating mode M2					0x3500		22										0x3500		22				0x3500		22
Current operating mode M3					0x4500		22
Installations Actual power					0xA38F	0..200 0..1	2	0xA38F	0..200 0..1	2	0xA38F	0..200 0..1	2	0xA38F	0..200 0..1	2	0xA38F	0..200 0..1	2				0xA38F	0..200 0..1	2
boiler output								0xA305	0..200 0..1	2				0xA305	0..200 0..1	2	0xA305	0..200 0..1	2				0xA305	0..200 0..1	2

features
Maximum reached exhaust gas temp. / Reset to default								0x08A1	0	2				0x08A1	0	2	0x08A1	0	2				0x08A1	0	2

Operation (read write)
operating mode					0x2301		1				0x2323		1	0x2301		1	0x2301		1	0x2301 can not wite :-( 0x2323 read + write ok :-)		1 1	0x2301		1							0x2301		1
saving mode					0x2302	0..1	1				0x2302	0..1	1	0x2302	0..1	1	0x2302	0..1	1				0x2302	0..1	1
Party mode					0x2303	0..1	1				0x2303	0..1	1	0x2303	0..1	1	0x2303	0..1	1				0x2303	0..1	1
Heating characteristic level					0x2304		1							0x2304		1	0x2304		1
Heating characteristic inclination					0x2305	/ 10	1							0x2305	/ 10	1	0x2305	/ 10	1
Room temperature					0x2306	3..37	1										0x2306	3..37	1
Red room temperature					0x2307	3..37	1										0x2307	3..37	1
Party temperature target					0x2308	3..37	1										0x2308	3..37	1
Operation (read write)
Room temperature																													0x2000	/ 10	2
Red room temperature																													0x2001	/ 10	2
Party room temperature Soll																													0x2022	/ 10	2
Heating characteristic level																													0x2006	/ 10	2
Heating curve gradient																													0x2007	/ 10	2

Operating state detailed
operating mode					0x2501		1	0x2501		1	0x2501		1	0x2501		1	0x2501		1				0x2501		1
Timer heating-up phase					0x2502	/ 10	4							0x2502	/ 10	4	0x2502	/ 10	4				0x2502	/ 10	4
Hot water release					0x2508		1	0x2508		1				0x2508		1	0x2508		1				0x2508		1
Heating circuit					0x250A		1							0x250A		1	0x250A		1				0x250A		1
room control switching					0x250B		1							0x250B		1	0x250B		1				0x250B		1
Room setpoint temperature					0x250C	/ 10	2				0x250C	/ 10	2	0x250C	/ 10	2	0x250C	/ 10	2				0x250C	/ 10	2
danger of frost					0x2510		1				0x2510		1	0x2510		1	0x2510		1				0x2510		1

heat pump
Primary circuit flow temperature (air)																													0x0103	/ 10	2
Primary circuit return temperature (air)																													0x0104	/ 10	2
Secondary circuit supply temperature (water)		0x0105	/ 10	2																									0x0105	/ 10	2
Secondary circuit return temperature (water)		0x0106	/ 10	2																									0x0106	/ 10	2
Pressure in the evaporator																													0x0680	/ 10	2
Pressure in the condenser																													0x0682	/ 10	2
Temperature in the evaporator																													0x0102	/ 10	2
Operating hours compressors																													0x0580	sec	4
Operating hours Primary source																													0x0582	sec	4
Operating hours Secondary source																													0x0584	sec	4
Operating hours Step 1																													0x0588	sec	4
Operating hours Level 2																													0x0589	sec	4
Operating hours Heating circuit A1																													0x058D	sec	4
Operating hours Heating circuit M2																													0x058E	sec	4
Operating hours Heating circuit M3																													0x058F	sec	4
Operating hours Additional output (Z-pump)																													0x0590	sec	4
Operating hours																													0x0591	sec	4
Operating hours Switchover valve Heating / Warmw.																													0x0594	sec	4
Operating hours Storage charging pump																													0x0596	sec	4
Number of compressors																													0x0500		4
Number of inputs Primary source																													0x0502		4
Number of secondary sources		0x0504	CO	4																									0x0504		4
Number of cycles Step 1																													0x0508		4
Number of cycles Level 2																													0x0509		4
Number of circuits Heating circuit A1																													0x050D		4
Number of heating circuits M2																													0x050E		4
Number of switch-on circuits M3																													0x050F		4
Number of inputs Additional output (Z-pump)																													0x0510		4
Number of activations Collective message																													0x0511		4
Number of switching-on switch-over valve heating / hot water																													0x0514		4
Number of power-ups Memory charging pump																													0x0516		4
Status Compressor On / Off																													0x0400	0..1	1
Status Primary Source On / Off																													0x0402	0..1	1
Status Secondary source On / Off																													0x0404	0..1	1
Status Flow rate. Level1 On / Off																													0x0408	0..1	1
Status Flow rate. Level2 On / Off																													0x0409	0..1	1
Status Pump Heating circuit A1 On / Off																													0x040D	0..1	1
Status Pump Heating circuit M2 On / Off																													0x040E	0..1	1
Status Pump Heating circuit M3 On / Off																													0x040F	0..1	1
Status Additional output (Z-pump) On / Off																													0x0410	0..1	1
Status group message On / Off																													0x0411	0..1	1
Status Switchover valve Heating / Hot water On / Off		0x494		2																									0x0414	0..1	1
Status Storage charge pump On / Off																													0x0416	0..1	1

Pellet and log wood boiler
Buffer temperature damped above																																0x0810	/ 10	2
Buffer temperature steamed down																																0x0812	/ 10	2
boiler temperature																																0x0B12	/ 10	2
flame temperature																																0x0B14	/ 10	2
insertion temperature																																0x0B16	/ 10	2
Lambdason [%]																																0x0B18	/ 10	2
Position primary air flap																																0x0B1A	0..100	1
Position secondary air flap																																0x0B1B	0..100	1
Speed ​​setpoint																																0x0B1C	0..3000	2
Speed ​​Is																																0x0B1E	0..3000	2
Boiler performance [%]																																0x0B20	0..100	1
Fuel consumption [kg]																																0x08B0		4

## 20CB
Model	VScotHO1
	addr	fact.	bytes
equipment identity	0x00F8	20CB	2
Storage temperature 2 (sensor 5B)	0x0806	/ 10	2
Exhaust gas temperature (sensor 15)	0x0808	/ 10	2
Boiler temperature low	0x0810	/ 10	2
Storage temperature low	0x0812	/ 10	2
Storage temperature 2 low	0x0814	/ 10	2
Cylinder primary pump	0x0845	0..1	1
circulation pump	0x0846	0..1	1
collective fault	0x0847	0..1	1
burner starts	0x088A		4
Room temperature A1M1 lowpass	0x0896	/ 10	2
Room temperature M2 low-pass	0x0898	/ 10	2
Maximum reached exhaust gas temp. Reset to default	0x08A1	0	2
Operating hours Stage 1	0x08A7	sec	4
Nominal speed of heating circuit pump M2	0x0A3B		1
Set speed Internal pump	0x0A3C	0..100	1
operating mode	0x2301		1
saving mode	0x2302	0..1	1
Party mode	0x2303	0..1	1
Current operating mode A1M1	0x2500		22
operating mode	0x2501		1
Timer heating-up phase	0x2502	/ 10	4
Hot water release	0x2508		1
Heating circuit	0x250A		1
room control switching	0x250B		1
Room setpoint temperature	0x250C	/ 10	2
danger of frost	0x2510		1
Pre-flow setpoint temperature A1M1	0x2544	/ 10	2
Mixing position M1 (0..100%)	0x254C	/ 2	1
Current operating mode M2	0x3500		22
Room temperature temperature actual M2	0x350C	/ 10	2
Pre-flow setpoint temperature M2	0x3544	/ 10	2
Flow temperature M2	0x3900	/ 10	2
Heating circuit pump M2	0x3906	0..1	1
Outside temperature low	0x5525	/ 10	2
Outside temperature dampened	0x5527	/ 10	2
Throttle valve position (0..100%)	0x5555	/ 2	1
Boiler temperature	0x555A	/ 10	2
reheating	0x6551	0..1	1
solar pump	0x6552	0..1	1
heat	0x6560	kWh	4
collector temperature	0x6564	/ 10	2
storage temperature	0x6566	/ 10	2
operating hours	0x6568		2
Solar Info	0x7754		1
boiler output	0xA305	0..200 0..1	2
Current performance (0..100%)	0xA38F	/ 2	1
Installations Actual power	0xA38F	0..200 0..1	2